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2026 Lead and Copper Overview
Trussville Gas and Water system currently samples for Lead and Copper on a reduced monitoring schedule of every three years as required by the Environmental Protection Agency (EPA) Lead and Copper Rule and Alabama Department of Environmental Management (ADEM) regulations 335-11-7-.06 and 335-11-7-.07. 
Currently 30 (Tier 1) sample locations within the water system have been selected based on certain criteria set by ADEM and EPA regulations. Attached is a list of 30 (Tier 1) primary sites and 10 (Tier 1) alternate sites that will be used for collection of samples. 
Due to an increase in security measures, the sites listed within this collection area contain no homeowner names, just addresses within the water system.
 MATERIAL INVENTORY
Trussville Gas and Water system currently services approximately 256 miles of water lines within its distribution system and approximately 13,000 customers.  The 256 miles of water lines are comprised of approximately 230 miles of iron piping, 25 miles of PVC piping and 1 mile of galvanized piping.   Brass fittings within the distribution system are of compression type and effective as of 2014 are the mandated low lead requirement. Of the approximate 13,000 water meters located within the distribution system and due to an AMR change out program, all of our water meters are low lead compliant and contain the NSF/ANSI 61-G certification. Meter loops prior to 2014 may contain lead alloys and are currently being replaced with the mandated low lead fittings when encountered during maintenance.

Within the water distribution system are items that contain some of the following Lead and Copper:
 
· Brass fittings and meter loops on service lines installed before 2014 that contain lead alloy.
· Internal fire hydrant components 
· Customer homes with lead components and lead solder plumbing fixtures.
· Copper service lines.
· Customer Homes containing some copper plumbing fixtures and piping.

Approximately 85% of the service lines up to the water meter within the central area of the distribution system are of type k copper, in the Northern area of the system 10% are of plastic and some southern area parts are approximately 5 % galvanized. All new installations and repairs are performed and installed with low lead compliant fittings with the NSF/ANSI 61-G certifications.
The fittings and materials installed past the water meter varies from polyethylene, copper and galvanized, and are the responsibility of the owner.   We estimate that 90% of the homes and structures may contain possible lead alloys and lead solder along with copper plumbing.  Of that 90%, approximately 25% were built before 1983. Trussville Gas and Water has completed the Lead Service Line Inventory and has found no lead service lines (LSL) within the Trussville Gas and Water distribution system.
For any questions or information concerning the Trussville Gas and Water system materials inventory please contact:
Trussville Gas and Water
 (205) 655-3211 
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